## Weather Comp chart
Weather Compensation Chart parameters: | [5 empty] | Weather Compensation Chart parameters: | [5 empty] | Weather Compensation Chart parameters:
| 2104 Minimum Ambient Temp °C | 0 | 2103 Minimum Water Temp °C | 30 | 0.6 |  | 2104 Minimum Ambient Temp °C | -1 | 2103 Minimum Water Temp °C | 30 | 0.57143 |  | 2104 Minimum Ambient Temp °C | -2 | 2103 Minimum Water Temp °C | 30 | 0.54545
| 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 42 | change / °C |  | 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 42 | change / °C |  | 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 42 | change / °C
| Air temperature °C | 0 | Heating Temperature °C | 42 |  |  | Air temperature °C | -1 | Heating Temperature °C | 42 |  |  | Air temperature °C | -2 | Heating Temperature °C | 42
|  | 1 |  | 41.4 |  |  |  | 0 |  | 41.4286 |  |  |  | -1 |  | 41.4545
|  | 2 |  | 40.8 |  |  |  | 1 |  | 40.8571 |  |  |  | 0 |  | 40.9091
|  | 3 |  | 40.2 |  |  |  | 2 |  | 40.2857 |  |  |  | 1 |  | 40.3636
|  | 4 |  | 39.6 |  |  |  | 3 |  | 39.7143 |  |  |  | 2 |  | 39.8182
|  | 5 |  | 39 | 20c |  |  | 4 |  | 39.1429 |  |  |  | 3 |  | 39.2727
|  | 6 |  | 38.4 |  |  |  | 5 |  | 38.5714 |  |  |  | 4 |  | 38.7273
|  | 7 |  | 37.8 |  |  |  | 6 |  | 38 |  |  |  | 5 |  | 38.1818
|  | 8 |  | 37.2 |  |  |  | 7 |  | 37.4286 |  |  |  | 6 |  | 37.6364
|  | 9 |  | 36.6 |  |  |  | 8 |  | 36.8571 |  |  |  | 7 |  | 37.0909
|  | 10 |  | 36 |  |  |  | 9 |  | 36.2857 |  |  |  | 8 |  | 36.5455
|  | 11 |  | 35.4 |  |  |  | 10 |  | 35.7143 |  |  |  | 9 |  | 36
|  | 12 |  | 34.8 |  |  |  | 11 |  | 35.1429 |  |  |  | 10 |  | 35.4545
|  | 13 |  | 34.2 |  |  |  | 12 |  | 34.5714 |  |  |  | 11 |  | 34.9091
|  | 14 |  | 33.6 |  |  |  | 13 |  | 34 |  |  |  | 12 |  | 34.3636
|  | 15 |  | 33 |  |  |  | 14 |  | 33.4286 |  |  |  | 13 |  | 33.8182
|  | 16 |  | 32.4 |  |  |  | 15 |  | 32.8571 |  |  |  | 14 |  | 33.2727
|  | 17 |  | 31.8 |  |  |  | 16 |  | 32.2857 |  |  |  | 15 |  | 32.7273
|  | 18 |  | 31.2 |  |  |  | 17 |  | 31.7143 |  |  |  | 16 |  | 32.1818
|  | 19 |  | 30.6 |  |  |  | 18 |  | 31.1429 |  |  |  | 17 |  | 31.6364
|  | 20 |  | 30 |  |  |  | 19 |  | 30.5714 |  |  |  | 18 |  | 31.0909
Weather Compensation Chart parameters: | [5 empty] | Weather Compensation Chart parameters: | [5 empty] | Weather Compensation Chart parameters:
| 2104 Minimum Ambient Temp °C | 0 | 2103 Minimum Water Temp °C | 30 | 0.55 |  | 2104 Minimum Ambient Temp °C | -1 | 2103 Minimum Water Temp °C | 30 | 0.52381 |  | 2104 Minimum Ambient Temp °C | -2 | 2103 Minimum Water Temp °C | 30 | 0.5
| 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 41 | change / °C |  | 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 41 | change / °C |  | 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 41 | change / °C
| Air temperature °C | 0 | Heating Temperature °C | 41 |  |  | Air temperature °C | -1 | Heating Temperature °C | 41 |  |  | Air temperature °C | -2 | Heating Temperature °C | 41
|  | 1 |  | 40.45 |  |  |  | 0 |  | 40.4762 |  |  |  | -1 |  | 40.5
|  | 2 |  | 39.9 |  |  |  | 1 |  | 39.9524 |  |  |  | 0 |  | 40
|  | 3 |  | 39.35 |  |  |  | 2 |  | 39.4286 |  |  |  | 1 |  | 39.5
|  | 4 |  | 38.8 |  |  |  | 3 |  | 38.9048 |  |  |  | 2 |  | 39
|  | 5 |  | 38.25 |  |  |  | 4 |  | 38.381 |  |  |  | 3 |  | 38.5
|  | 6 |  | 37.7 |  |  |  | 5 |  | 37.8571 |  |  |  | 4 |  | 38
|  | 7 |  | 37.15 |  |  |  | 6 |  | 37.3333 |  |  |  | 5 |  | 37.5
|  | 8 |  | 36.6 |  |  |  | 7 |  | 36.8095 |  |  |  | 6 |  | 37
|  | 9 |  | 36.05 |  |  |  | 8 |  | 36.2857 |  |  |  | 7 |  | 36.5
|  | 10 |  | 35.5 |  |  |  | 9 |  | 35.7619 |  |  |  | 8 |  | 36
|  | 11 |  | 34.95 |  |  |  | 10 |  | 35.2381 |  |  |  | 9 |  | 35.5
|  | 12 |  | 34.4 |  |  |  | 11 |  | 34.7143 |  |  |  | 10 |  | 35
|  | 13 |  | 33.85 |  |  |  | 12 |  | 34.1905 |  |  |  | 11 |  | 34.5
|  | 14 |  | 33.3 |  |  |  | 13 |  | 33.6667 |  |  |  | 12 |  | 34
|  | 15 |  | 32.75 |  |  |  | 14 |  | 33.1429 |  |  |  | 13 |  | 33.5
|  | 16 |  | 32.2 |  |  |  | 15 |  | 32.619 |  |  |  | 14 |  | 33
|  | 17 |  | 31.65 |  |  |  | 16 |  | 32.0952 |  |  |  | 15 |  | 32.5
|  | 18 |  | 31.1 |  |  |  | 17 |  | 31.5714 |  |  |  | 16 |  | 32
|  | 19 |  | 30.55 |  |  |  | 18 |  | 31.0476 |  |  |  | 17 |  | 31.5
|  | 20 |  | 30 |  |  |  | 19 |  | 30.5238 |  |  |  | 18 |  | 31
Weather Compensation Chart parameters: | [5 empty] | Weather Compensation Chart parameters: | [5 empty] | Weather Compensation Chart parameters:
| 2104 Minimum Ambient Temp °C | 0 | 2103 Minimum Water Temp °C | 30 | 0.5 |  | 2104 Minimum Ambient Temp °C | -1 | 2103 Minimum Water Temp °C | 30 | 0.47619 |  | 2104 Minimum Ambient Temp °C | -2 | 2103 Minimum Water Temp °C | 30 | 0.45455
| 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 40 | change / °C |  | 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 40 | change / °C |  | 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 40 | change / °C
| Air temperature °C | 0 | Heating Temperature °C | 40 |  |  | Air temperature °C | -1 | Heating Temperature °C | 40 |  |  | Air temperature °C | -2 | Heating Temperature °C | 40
|  | 1 |  | 39.5 |  |  |  | 0 |  | 39.5238 |  |  |  | -1 |  | 39.5455
|  | 2 |  | 39 |  |  |  | 1 |  | 39.0476 |  |  |  | 0 |  | 39.0909
|  | 3 |  | 38.5 |  |  |  | 2 |  | 38.5714 |  |  |  | 1 |  | 38.6364
|  | 4 |  | 38 |  |  |  | 3 |  | 38.0952 |  |  |  | 2 |  | 38.1818
|  | 5 |  | 37.5 |  |  |  | 4 |  | 37.619 |  |  |  | 3 |  | 37.7273
|  | 6 |  | 37 |  |  |  | 5 |  | 37.1429 |  |  |  | 4 |  | 37.2727
|  | 7 |  | 36.5 |  |  |  | 6 |  | 36.6667 |  |  |  | 5 |  | 36.8182
|  | 8 |  | 36 |  |  |  | 7 |  | 36.1905 |  |  |  | 6 |  | 36.3636
|  | 9 |  | 35.5 |  |  |  | 8 |  | 35.7143 |  |  |  | 7 |  | 35.9091
|  | 10 |  | 35 |  |  |  | 9 |  | 35.2381 |  |  |  | 8 |  | 35.4545
|  | 11 |  | 34.5 |  |  |  | 10 |  | 34.7619 |  |  |  | 9 |  | 35
|  | 12 |  | 34 |  |  |  | 11 |  | 34.2857 |  |  |  | 10 |  | 34.5455
|  | 13 |  | 33.5 |  |  |  | 12 |  | 33.8095 |  |  |  | 11 |  | 34.0909
|  | 14 |  | 33 |  |  |  | 13 |  | 33.3333 |  |  |  | 12 |  | 33.6364
|  | 15 |  | 32.5 |  |  |  | 14 |  | 32.8571 |  |  |  | 13 |  | 33.1818
|  | 16 |  | 32 |  |  |  | 15 |  | 32.381 |  |  |  | 14 |  | 32.7273
|  | 17 |  | 31.5 |  |  |  | 16 |  | 31.9048 |  |  |  | 15 |  | 32.2727
|  | 18 |  | 31 |  |  |  | 17 |  | 31.4286 |  |  |  | 16 |  | 31.8182
|  | 19 |  | 30.5 |  |  |  | 18 |  | 30.9524 |  |  |  | 17 |  | 31.3636
|  | 20 |  | 30 |  |  |  | 19 |  | 30.4762 |  |  |  | 18 |  | 30.9091
Weather Compensation Chart parameters: | [5 empty] | Weather Compensation Chart parameters: | [5 empty] | Weather Compensation Chart parameters:
| 2104 Minimum Ambient Temp °C | 0 | 2103 Minimum Water Temp °C | 30 | 0.45 |  | 2104 Minimum Ambient Temp °C | -1 | 2103 Minimum Water Temp °C | 30 | 0.42857 |  | 2104 Minimum Ambient Temp °C | -2 | 2103 Minimum Water Temp °C | 30 | 0.40909
| 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 39 | change / °C |  | 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 39 | change / °C |  | 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 39 | change / °C
| Air temperature °C | 0 | Heating Temperature °C | 39 |  |  | Air temperature °C | -1 | Heating Temperature °C | 39 |  |  | Air temperature °C | -2 | Heating Temperature °C | 39
|  | 1 |  | 38.55 |  |  |  | 0 |  | 38.5714 |  |  |  | -1 |  | 38.5455
|  | 2 |  | 38.1 |  |  |  | 1 |  | 38.1429 |  |  |  | 0 |  | 38.0909
|  | 3 |  | 37.65 |  |  |  | 2 |  | 37.7143 |  |  |  | 1 |  | 37.6364
|  | 4 |  | 37.2 |  |  |  | 3 |  | 37.2857 |  |  |  | 2 |  | 37.1818
|  | 5 |  | 36.75 |  |  |  | 4 |  | 36.8571 |  |  |  | 3 |  | 36.7273
|  | 6 |  | 36.3 |  |  |  | 5 |  | 36.4286 |  |  |  | 4 |  | 36.2727
|  | 7 |  | 35.85 |  |  |  | 6 |  | 36 |  |  |  | 5 |  | 35.8182
|  | 8 |  | 35.4 |  |  |  | 7 |  | 35.5714 |  |  |  | 6 |  | 35.3636
|  | 9 |  | 34.95 |  |  |  | 8 |  | 35.1429 |  |  |  | 7 |  | 34.9091
|  | 10 |  | 34.5 |  |  |  | 9 |  | 34.7143 |  |  |  | 8 |  | 34.4545
|  | 11 |  | 34.05 |  |  |  | 10 |  | 34.2857 |  |  |  | 9 |  | 34
|  | 12 |  | 33.6 |  |  |  | 11 |  | 33.8571 |  |  |  | 10 |  | 33.5455
|  | 13 |  | 33.15 |  |  |  | 12 |  | 33.4286 |  |  |  | 11 |  | 33.0909
|  | 14 |  | 32.7 |  |  |  | 13 |  | 33 |  |  |  | 12 |  | 32.6364
|  | 15 |  | 32.25 |  |  |  | 14 |  | 32.5714 |  |  |  | 13 |  | 32.1818
|  | 16 |  | 31.8 |  |  |  | 15 |  | 32.1429 |  |  |  | 14 |  | 31.7273
|  | 17 |  | 31.35 |  |  |  | 16 |  | 31.7143 |  |  |  | 15 |  | 31.2727
|  | 18 |  | 30.9 |  |  |  | 17 |  | 31.2857 |  |  |  | 16 |  | 30.8182
|  | 19 |  | 30.45 |  |  |  | 18 |  | 30.8571 |  |  |  | 17 |  | 30.3636
|  | 20 |  | 30 |  |  |  | 19 |  | 30.4286 |  |  |  | 18 |  | 29.9091
Weather Compensation Chart parameters: | [5 empty] | Weather Compensation Chart parameters: | [5 empty] | Weather Compensation Chart parameters:
| 2104 Minimum Ambient Temp °C | 0 | 2103 Minimum Water Temp °C | 30 | 0.4 |  | 2104 Minimum Ambient Temp °C | -1 | 2103 Minimum Water Temp °C | 30 | 0.38095 |  | 2104 Minimum Ambient Temp °C | -2 | 2103 Minimum Water Temp °C | 30 | 0.36364
| 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 38 | change / °C |  | 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 38 | change / °C |  | 2105 Maximum Ambient Temp °C | 20 | 2102 Maximum Water Temp °C | 38 | change / °C
| Air temperature °C | 0 | Heating Temperature °C | 38 |  |  | Air temperature °C | -1 | Heating Temperature °C | 38 |  |  | Air temperature °C | -2 | Heating Temperature °C | 38
|  | 1 |  | 37.5 |  |  |  | 0 |  | 37.5238 |  |  |  | -1 |  | 37.5455
|  | 2 |  | 37 |  |  |  | 1 |  | 37.0476 |  |  |  | 0 |  | 37.0909
|  | 3 |  | 36.5 |  |  |  | 2 |  | 36.5714 |  |  |  | 1 |  | 36.6364
|  | 4 |  | 36 |  |  |  | 3 |  | 36.0952 |  |  |  | 2 |  | 36.1818
|  | 5 |  | 35.5 |  |  |  | 4 |  | 35.619 |  |  |  | 3 |  | 35.7273
|  | 6 |  | 35 |  |  |  | 5 |  | 35.1429 |  |  |  | 4 |  | 35.2727
|  | 7 |  | 34.5 |  |  |  | 6 |  | 34.6667 |  |  |  | 5 |  | 34.8182
|  | 8 |  | 34 |  |  |  | 7 |  | 34.1905 |  |  |  | 6 |  | 34.3636
|  | 9 |  | 33.5 |  |  |  | 8 |  | 33.7143 |  |  |  | 7 |  | 33.9091
|  | 10 |  | 33 |  |  |  | 9 |  | 33.2381 |  |  |  | 8 |  | 33.4545
|  | 11 |  | 32.5 |  |  |  | 10 |  | 32.7619 |  |  |  | 9 |  | 33
|  | 12 |  | 32 |  |  |  | 11 |  | 32.2857 |  |  |  | 10 |  | 32.5455
|  | 13 |  | 31.5 |  |  |  | 12 |  | 31.8095 |  |  |  | 11 |  | 32.0909
|  | 14 |  | 31 |  |  |  | 13 |  | 31.3333 |  |  |  | 12 |  | 31.6364
|  | 15 |  | 30.5 |  |  |  | 14 |  | 30.8571 |  |  |  | 13 |  | 31.1818
|  | 16 |  | 30 |  |  |  | 15 |  | 30.381 |  |  |  | 14 |  | 30.7273
|  | 17 |  | 29.5 |  |  |  | 16 |  | 29.9048 |  |  |  | 15 |  | 30.2727
|  | 18 |  | 29 |  |  |  | 17 |  | 29.4286 |  |  |  | 16 |  | 29.8182
|  | 19 |  | 28.5 |  |  |  | 18 |  | 28.9524 |  |  |  | 17 |  | 29.3636
|  | 20 |  | 28 |  |  |  | 19 |  | 28.4762 |  |  |  | 18 |  | 28.9091

## Holding Reg R-W
HOLDING REGISTER - READ/WRITE | All 16-bit signed
Address | Address(hex) | Holding Register | Holding Register(hex) | Holding Register (binary) | Default Value | Scale | Parameter | Description
0 | 0 | 0 | 0 | 00000000 00000000
1 | 1 | 0 | 0 | 00000000 00000000
2 | 2 | 450 | 01C2 | 00000001 11000010 | 45 | 0.5°C | 21 01 | Heating Zone1, Fixed Outgoing water set point in Heating
3 | 3 | 450 | 01C2 | 00000001 11000010 | 45 | 0.5°C | 21 02 | Max. Outgoing water temperature in Heating mode (Tm1) Zone1
4 | 4 | 300 | 012C | 00000001 00101100 | 30 | 0.5°C | 21 03 | Min. Outgoing water temperature in Heating mode (Tm2) Zone1
5 | 5 | 40 | 28 | 00000000 00101000 | 0 | 0.5°C | 21 04 | Min. Outdoor air temperature corresponding to max. Outgoing water temperature (Te1) Zone1
6 | 6 | 200 | 00C8 | 00000000 11001000 | 20 | 0.5°C | 21 05 | Max. Outdoor air temperature corresponding to min. Outgoing water temperature (Te2) Zone1
7 | 7 | 450 | 01C2 | 00000001 11000010 | 45 | 0.5°C | 21 11 | Heating one2, ixed Outgoing water et point in Heating.
8 | 8 | 450 | 01C2 | 00000001 11000010 | 45 | 0.5°C | 21 12 | Max. Outgoing water temperature in Heating mode (Tm1) Zone2
9 | 9 | 300 | 012C | 00000001 00101100 | 30 | 0.5°C | 21 13 | Min. Outgoing water temperature in Heating mode (Tm2) Zone2
10 | 000A | 0 | 0 | 00000000 00000000 | 0 | 0.5°C | 21 14 | Min. Outdoor air temperature corresponding to max. Outgoing water temperature (Te1) Zone2
11 | 000B | 200 | 00C8 | 00000000 11001000 | 20 | 0.5°C | 21 15 | Max. Outdoor air temperature corresponding to max. Outgoing water temperature (Te2) Zone2
12 | 000C | 70 | 46 | 00000000 01000110 | 7 | 0.5°C | 21 21 | Heating Zone2, Fixed Outgoing water set point in Heating.
13 | 000D | 200 | 00C8 | 00000000 11001000 | 20 | 0.5°C | 21 22 | Max. Outgoing water temperature in Cooling mode (Tm1) Zone1
14 | 000E | 180 | 00B4 | 00000000 10110100 | 18 | 0.5°C | 21 23 | Min. Outgoing water temperature in Cooling mode (Tm2) Zone1
15 | 000F | 250 | 00FA | 00000000 11111010 | 25 | 0.5°C | 21 24 | Min. Outdoor air temperature corresponding to max. Outgoing water temperature (Te1) Zone1
16 | 10 | 350 | 015E | 00000001 01011110 | 35 | 0.5°C | 21 25 | Max. Outdoor air temperature corresponding to max. Outgoing water temperature (Te2) Zone1
17 | 11 | 70 | 46 | 00000000 01000110 | 7 | 0.5°C | 21 31 | Cooling Zone2, Fixed Outgoing water set point in Cooling
18 | 12 | 200 | 00C8 | 00000000 11001000 | 20 | 0.5°C | 21 32 | Max. Outgoing water temperature in Cooling mode (Tm1) Zone2
19 | 13 | 180 | 00B4 | 00000000 10110100 | 18 | 0.5°C | 21 33 | Min. Outgoing water temperature in Cooling mode (Tm2) Zone2
20 | 14 | 250 | 00FA | 00000000 11111010 | 25 | 0.5°C | 21 34 | Min. Outdoor air temperature corresponding to max. Outgoing water temperature (Te1) Zone2
21 | 15 | 350 | 015E | 00000001 01011110 | 35 | 0.5°C | 21 35 | Max. Outdoor air temperature corresponding to max. Outgoing water temperature (Te2) Zone2
22 | 16 | 80 | 50 | 00000000 01010000 | 8 | 0.5°C | 21 41 | Hysteresis of water set point in Heating and DHW
23 | 17 | 80 | 50 | 00000000 01010000 | 8 | 0.5°C | 21 42 | Hysteresis of water set point in Cooling
24 | 18 | 50 | 32 | 00000000 00110010 | 5 | 0.5°C | 21 51 | Low tariff deferential water set point for Heating
25 | 19 | 50 | 32 | 00000000 00110010 | 5 | 0.5°C | 21 52 | Low tariff deferential water set point for Cooling
26 | 001A | 1 | 1 | 00000000 00000001 | 0 |  | 31 01 | DHW production priority setting 0=DHW is unavailable 1=DHW is available, and priority DHW over space Heating 2=DHW is available, and priority space Heating over DHW
27 | 001B | 1 | 1 | 00000000 00000001 | 1 |  | 31 02 | Type of configuration to heat the DHW 0=Heat pump + Heater 1=Heat pump only 2=Heater only
28 | 001C | 500 | 01F4 | 00000001 11110100 | 50 | 0.5°C | 31 11 | DHW Comfort set temperature
29 | 001D | 400 | 190 | 00000001 10010000 | 40 | 0.5°C | 31 12 | DHW Economy set temp
30 | 001E | 30 | 001E | 00000000 00011110 | 3 | 0.5°C | 31 13 | DHW Set point hysterisis
31 | 001F | 600 | 258 | 00000010 01011000 | 60 | 0.5°C | 31 14 | DHW Over boost mode set point
32 | 20 | 61 | 003D | 00000000 00111101 |  | 1min | 31 21 | Max. time for DHW request
33 | 21 | 30 | 001E | 00000000 00011110 | 30 | 1min | 31 31 | Delay time on DHW heater from OFF compressor
34 | 22 | 65486 | FFCE | 11111111 11001110 |  | 0.5°C | 31 33 | Outdoor air temperature to enable DHW heaters
35 | 23 | 50 | 32 | 00000000 00110010 |  | 0.5°C | 31 34 | Outdoor air temperature hysteresis to disable DHW heater
36 | 24 | 650 | 028A | 00000010 10001010 |  | 0.5°C | S 31 44 | Anti-legionella set point
37 | 25 | 80 | 50 | 00000000 01010000 |  | % | 41 11 | Max. frequency of Night mode
38 | 26 | 0 | 0 | 00000000 00000000 |  | 1sec | 41 21 | Min. time compressor ON – OFF time
39 | 27 | 30 | 001E | 00000000 00011110 |  | 1sec | 41 22 | Delay time pump OFF from compressor OFF
40 | 28 | 30 | 001E | 00000000 00011110 |  | 1sec | 41 23 | Delay time compressor ON from pump ON
41 | 29 | 0 | 0 | 00000000 00000000 |  |  | 42 00 | Type of configuration of Main water pump 00 0=always ON, 1=ON/OFF based on Buffer tank temperature 2=ON/OFF based on Sniffing cycles
42 | 002A | 3 | 3 | 00000000 00000011 |  | 1min | 42 01 | Time ON Main water pump for Sniffing cycle.
43 | 002B | 5 | 5 | 00000000 00000101 |  | 1min | 42 02 | Time OFF Main water pump
44 | 002C | 3 | 3 | 00000000 00000011 |  | 1min | 42 03 | Delay time OFF Main water pump from OFF compressor
45 | 002D | 48 | 30 | 00000000 00110000 |  | 1hr | 42 11 | OFF time for Unlock pump function start
46 | 002E | 5 | 5 | 00000000 00000101 |  | 1sec | 42 12 | Time ON Main water pump for Unlock pump function
47 | 002F | 5 | 5 | 00000000 00000101 |  | 1sec | 42 13 | Time ON water pump1 for Unlock pump function
48 | 30 | 5 | 5 | 00000000 00000101 |  | 1sec | 42 14 | Time ON water pump2 for Unlock pump function
49 | 31 | 0 | 0 | 00000000 00000000 |  |  | 42 20 | Type of operation of additional water pump 0=disable 1=depending on Main water pump setting 2=depending on Main water pump setting but always OFF when the DHW mode is activated 3= always ON, apart if any alarms are activated or if the HP unit is in OFF mode 4=ON/OFF based on Room air temperature
50 | 32 | 140 | 008C | 00000000 10001100 |  | 0.5°C | 43 01 | Start temperature of Frost protection on Room air 14.0 temperature
51 | 33 | 10 | 000A | 00000000 00001010 |  | 0.5°C | 43 02 | Hysteresis of Room air temperature of Frost protection
52 | 34 | 350 | 015E | 00000001 01011110 |  | 0.5°C | 43 03 | Water temperature of Frost protection
53 | 35 | 30 | 001E | 00000000 00011110 |  | 1sec | 43 04 | Delay time OFF Main water pump from OFF Frost protection operation function
54 | 36 | 40 | 28 | 00000000 00101000 |  | 0.5°C | 43 11 | Start temperature of Frost protection on Outdoor air temperature
55 | 37 | 30 | 001E | 00000000 00011110 |  | 0.5°C | 43 12 | Hysteresis of Outdoor air temperature
56 | 38 | 40 | 28 | 00000000 00101000 |  | 0.5°C | 43 13 | Backup heater set point during Frost protection
57 | 39 | 30 | 001E | 00000000 00011110 |  | 0.5°C | 43 14 | Hysteresis of Outgoing water temperature
58 | 003A | 50 | 32 | 00000000 00110010 |  | 0.5°C | 43 31 | Start temperature of Frost protection on DHW tank temperature
59 | 003B | 30 | 001E | 00000000 00011110 |  | 0.5°C | 43 32 | Hysteresis of DHW tank temperature
60 | 003C | 60 | 003C | 00000000 00111100 |  | % | 44 01 | Room relative humidity value
61 | 003D | 55 | 37 | 00000000 00110111 |  | % | 44 11 | Room relative humidity value to start increasing Outgoing water temperature set point
62 | 003E | 100 | 64 | 00000000 01100100 | 10 | 0.5°C | 44 12 | Max. Outgoing temperature hysteresis corresponding to 100% relative humidity
63 | 003F | 12 | 000C | 00000000 00001100 |  | 10sec | 45 01 | Mixing valve runtime (from the fully closed to the fully 120 open position)
64 | 40 | 6 | 6 | 00000000 00000110 |  | 10sec | 45 02 | Mixing valve integral factor
65 | 41 | 500 | 01F4 | 00000001 11110100 |  | 0.5°C | 45 03 | Max Water temperature in mixing circuit
66 | 42 | 60 | 003C | 00000000 00111100 |  | 1sec | 45 11 | 3way valve change over time
67 | 43 | 15 | 000F | 00000000 00001111 |  | 1sec | 45 21 | Flow switch alarm delay time at. Pump start up
68 | 44 | 2 | 2 | 00000000 00000010 |  | 1sec | 45 22 | Flow switch alarm delay time in steady operation of the water pump
69 | 45 | 5 | 5 | 00000000 00000101 |  |  | 45 23 | The number of retry until displaying alarm
70 | 46 | 60 | 003C | 00000000 00111100 |  | 1min | 45 24 | The time of repeating retry until displaying alarm
71 | 47 | 0 | 0 | 00000000 00000000 |  |  | 46 00 | Backup heater type of function 0=disable 1=Replacement mode 2=Emergency mode 3=Supplementary mode
72 | 48 | 500 | 01F4 | 00000001 11110100 |  | 0.5°C | 46 01 | manual water set point
73 | 49 | 50 | 32 | 00000000 00110010 |  | 0.5°C | 46 02 | Manual water temp hysteris
74 | 004A | 10 | 000A | 00000000 00001010 |  | 1sec | 46 03 | Delay time of the heater OFF that avoid flow switch alarm
75 | 004B | 5 | 5 | 00000000 00000101 |  | 1min | 46 04 | Heater Activation delay time
76 | 004C | 598 | 256 | 00000010 01010110 |  | 1°C*sec | 46 05 | Integration time for backup heater
77 | 004D | 65486 | FFCE | 11111111 11001110 |  | 0.5°C | 46 11 | Outdoor air temperature to enable Backup heaters and disable compressor
78 | 004E | 50 | 32 | 00000000 00110010 |  | 0.5°C | 46 12 | Outdoor air temperature hysteresis to disable Backup heaters and enable compressor
79 | 004F | 50 | 32 | 00000000 00110010 |  | 0.5°C | 46 13 | Outdoor air temperature to enable Backup heaters (Supplementary mode)
80 | 50 | 50 | 32 | 00000000 00110010 |  | 0.5°C | 46 14 | Outdoor air temperature hysteresis to disable Backup heaters (Supplementary mode)
81 | 51 | 0 | 0 | 00000000 00000000 |  |  | 46 20 | Freeze protection functions 0=disable 1=enabled during Start-up 2=enabled during Defrost 3=enabled during Start-up and Defrost
82 | 52 | 80 | 50 | 00000000 01010000 |  | 0.5°C | 46 21 | Outgoing water temperature set point during Start-up
83 | 53 | 50 | 32 | 00000000 00110010 |  | 0.5°C | 46 22 | Hysteresis water temperature set point during Start-up
84 | 54 | 0 | 0 | 00000000 00000000 |  |  | 47 00 | EHS type of function 0=disable 1=Replacement mode 2=Supplementary mode
85 | 55 | 65486 | FFCE | 11111111 11001110 |  | 0.5°C | 47 02 | Outdoor air temperature to enable EHS and disable compressor
86 | 56 | 50 | 32 | 00000000 00110010 |  | 0.5°C | 47 03 | Outdoor air temperature hysteresis to disable EHS and enable compressor
87 | 57 | 50 | 32 | 00000000 00110010 |  | 0.5°C | 47 04 | Outdoor air temperature to enable EHS(Supplementary mode)
88 | 58 | 50 | 32 | 00000000 00110010 |  | 0.5°C | 47 05 | Outdoor air temperature hysteresis to disable EHS(Supplementary mode)
89 | 59 | 5 | 5 | 00000000 00000101 |  | 1min | 47 06 | EHS activation delay time
90 | 005A | 64 | 40 | 00000000 01000000 |  | 1°C*sec | 47 07 | Integration time for starting EHS
91 | 005B | 1 | 1 | 00000000 00000001 |  |  | 51 20 | Terminal 20-21 : ON/OFF remote contact or EHS Alarm input 0=disable (Remote controller only) 1=ON/OFF remote contact 2=EHS Alarm input
92 | 005C | 0 | 0 | 00000000 00000000 |  |  | 51 24 | Terminal 24-25 : Heating/Cooling mode remote contact 0=disable (Remote controller only) 1= Cooling is CLOSE contact, Heating is OPEN contact. 2= Cooling is OPEN contact, Heating is CLOSE contact
93 | 005D | 0 | 0 | 00000000 00000000 |  |  | 51 47? | Terminal 47 : Alarm (Configurable output) 0=disable 1=Alarm 2=Ambient temperature reached
94 | 005E | 0 | 0 | 00000000 00000000
95 | 005F | 0 | 0 | 00000000 00000000 |  |  |  | RoomStat Master On/Off ??
96 | 60 | 0 | 0 | 00000000 00000000 |  |  |  | Roomstat Slave On/Off - unable to write
97 | 61 | 195 | 00C3 | 00000000 11000011 |  |  |  | Room set point target Master C
98 | 62 | 250 | 00FA | 00000000 11111010 |  |  |  | Room set point target Slave C
99 | 63 | 450 | 01C2 | 00000001 11000010
100 | 64 | 70 | 46 | 00000000 01000110
101 |  | 0
102 |  | 2

## Input Reg Read only
INPUT REGISTER - READ ONLY | All 16 bit signed
Address | Address(hex) | Input Register | Input register(hex) | Input Register (binary) | Units | Parameter | Description | Signed value | Home Assistant include
0 | 0 | 15 | 000F | 00000000 00001111 | 1°C | 01 00 | Return water temperature |  | y
1 | 1 | 0 | 0 | 00000000 00000000 | 1Hz | 01 01 | Compressor operating frequency |  | y
2 | 2 | 22 | 16 | 00000000 00010110 | 1°C | 01 02 | Discharge temperature |  | y
3 | 3 | 0 | 0 | 00000000 00000000 | 100W | 01 03 | Current consumption value |  | y
4 | 4 | 0 | 0 | 00000000 00000000 | 10rpm | 01 04 | Fan control number of rotation |  | y
5 | 5 | 12 | 000C | 00000000 00001100 | 1°C | 01 05 | Defrost temperature |  | y
6 | 6 | 12 | 000C | 00000000 00001100 | 1°C | 01 06 | Outdoor air temperature |  | y
7 | 7 | 0 | 0 | 00000000 00000000 | 100rpm | 01 07 | Water pump control number of rotation |  | y
8 | 8 | 19 | 13 | 00000000 00010011 | 1°C | 01 08 | Suction temperature |  | y
9 | 9 | 18 | 12 | 00000000 00010010 | 1°C | 01 09 | Outgoing water temperature |  | y
10 | 000A | 0 | 0 | 00000000 00000000 |  | 01 10 | Selected operating mode 0=Heating/Cooling OFF 1=Heating 2=Cooling
11 | 000B | 195 | 00C3 | 00000000 11000011 | 0.1°C | 01 11 | Room air set temperature of Zone1(Master) - Target temp
12 | 000C | 250 | 00FA | 00000000 11111010 | 0.1°C | 01 12 | Room air set temperature of Zone2(Slave)
13 | 000D | 0 | 0 | 00000000 00000000 |  | 01 13 | Selected DHW operating mode 0=disable 1=Comfort 2=Economy 3=Force
14 | 000E | 0 | 0 | 00000000 00000000 |  | 01 14 | Day 0=Monday, 1=Tuesday, 2=Wednesday, 3=Thursday, 4=Friday,5=Saturday, 6=Sunday
15 | 000F | 0 | 0 | 00000000 00000000
16 | 10 | 100 | 64 | 00000000 01100100 | 0.1°C | 01 31 | DHW tank temperature (Terminal 7-8)
17 | 11 | 65336 | FF38 | 11111111 00111000 | 0.1°C | 01 32 | Outdoor air temperature (Terminal 9-10) | -200
18 | 12 | 65336 | FF38 | 11111111 00111000 | 0.1°C | 01 33 | Buffer tank temperature (Terminal 11-12) | -200
19 | 13 | 65336 | FF38 | 11111111 00111000 | 0.1°C | 01 34 | Mix water temperature (Terminal 13-14) | -200
20 | 14 | 0 | 0 | 00000000 00000000 | % | 01 35 | Humidity Sensor (Terminal 18-19)
21 | 15 | 32381 | 7E7D | 01111110 01111101 |  | 01 50? | ?Current error code
22 | 16 | 32997 | 80F5 | 10000000 11100101 |  | 01 51? | ?Error code once before | -32539
23 | 17 | 32996 | 80F4 | 10000000 11100100 |  | 01 52? | ?Error code twice before | -32540
24 | 18 | 32995 | 80F3 | 10000000 11100011 |  | 01 53? | ?Error code three times before | -32541
25 | 19 | 32994 | 80F2 | 10000000 11100010 |  | 01 54? | ?Error code four times before | -32542
26 | 001A | 32993 | 80F1 | 10000000 11100001 |  | 01 55? | ?Error code five times before | -32543
27 | 001B | 32945 | 80B1 | 10000000 10110001 |  | 01 56? | ?Error code six times before | -32591
28 | 001C | 32381 | 7E7D | 01111110 01111101 |  | 01 57? | ?Error code seven times before | 32381
29 | 001D | 32381 | 7E7D | 01111110 01111101 |  | 01 58? | ?Error code eight times before | 32381
30 | 001E | 32381 | 7E7D | 01111110 01111101 |  | 01 59? | ?Error code nine times before | 32381
31 | 001F | 32381 | 7E7D | 01111110 01111101 |  | 01 60? | ?Error code ten times before | 32381
32 | 20 | 15 | 000F | 00000000 00001111 | 1°C | 01 72 | Plate Heat Exchanger Temp |  | y
33 | 21 | 220 | 00DC | 00000000 11011100 | 0.1°C |  | Indoor Master Temp Actual |  | y
34 | 22 | 400 | 190 | 00000001 10010000 | 0.1°C |  | Indoor Slave Temp Actual

## Coils Register
COILS REGISTER - READ/WRITE
Address | Address(hex) | Coil Value | Default Value | Controller Parameter | Description
0 | 0 | 0 |  |  | S01 61 Erase Error history??
1 | 1 | 1 |  | 03 00 | Operation at the time of reboot after blackout 0 = disable 1 = enable
2 | 2 | 1 |  | 21 00 | Heating Zone1, enable Outgoing water set point 0=Fixed set point 1=Climatic curve
3 | 3 | 0 |  | 21 10 | Heating Zone2, enable Outgoing water set point 0=Fixed set point 1=Climatic curve enabled
4 | 4 | 0 |  | 21 20 | Cooling Zone1, enable Outgoing water set point 0=Fixed set point 1=Climatic curve enabled
5 | 5 | 0 |  | 21 30 | Cooling Zone2, enable Outgoing water set point 0=Fixed set point 1=Climatic Curve Enabled
6 | 6 | 0 |  | 31 40 | Anti-legionella function 0=disable 1=enable
7 | 7 | 1 |  | 41 00 | The HP unit turns ON/OFF based on 0=Room set point 1 1=Water set point
8 | 8 | 1 |  | 43 00 | Frost protection on room temperature 0=disable 1 = enable
9 | 9 | 1 |  | 43 10 | Frost protection by outdoor temperature 0=disable 1 = enable
10 | 000A | 1 |  | 43 20 | Frost protection based on Outgoing water temperature 0=disable 1 = enable
11 | 000B | 1 |  | 43 30 | DHW storage frost protection 0=disable 1 = enable
12 | 000C | 1 |  | 43 40 | Secondary system circuit frost protection 0=disable 1 = enable
13 | 000D | 1 |  | 44 10 | Compensation for room humidity 0=disable 1=enable
14 | 000E | 1 |  | 46 10 | Conditions to be available Backup heaters 0= always enabled 1= dependent on Outdoor air temperature
15 | 000F | 1 |  | 47 01 | Conditions to be available Backup heaters 0= always enabled 1= dependent on Outdoor air temperature
16 | 10 | 1 |  | 51 01 | Terminal 1-2-3 : Remote Controller 1=enable
17 | 11 | 0 |  | 51 04 | Terminal 4-5-6 : 3way mixing valve 0=disable 1=enable
18 | 12 | 0 |  | 51 07 | Terminal 7-8 : DHW tank temperature probe 0=disable 1=enable
19 | 13 | 0 |  | 51 09 | Terminal 9-10 : Outdoor air temperature probe (additional) 0=disable 1=enable
20 | 14 | 0 |  | 51 11 | Terminal 11-12 : Buffer tank temperature probe 0=disable 1=enable
21 | 15 | 0 |  | 51 13 | Terminal 13-14 : Mix Water temperature probe 0=disable 1=enable
22 | 16 | 1 |  | 51 15 | Terminal 15-16-32 : RS485 Mod Bus 0=disable 1=enable
23 | 17 | 0 |  | 51 17 | Terminal 17-18 : Humidity sensor 0=disable 1=enable
24 | 18 | 1 |  | 51 19 | Terminal 19-18 : DHW remote contact 0=disable (Remote controller only) 1=enable
25 | 19 | 1 |  | 51 22 | Terminal 22-23 : Dual set point control 0=disable 1=enable
26 | 001A | 1 |  | 51 26 | Terminal 26-27 : Flow switch 0=disable 1=enable
27 | 001B | 0 |  | 51 28 | Terminal 28-29 : Night mode 0=disable (Remote controller only) 1=enable
28 | 001C | 0 |  | 51 30 | Terminal 30-31 : Low tariff 0=disable (Remote controller only) 1=enable
29 | 001D | 1 |  | 51 41 | Terminal 41-42 : EHS (External heat source for space heating) 0=disable 1=enable
30 | 001E | 0 |  | 51 43 | Terminal 43-44 : Heating/Cooling mode output 0=disable 1=Indication of Cooling mode (CLOSE=Cooling) 2=indication of Heating mode (CLOSE=Heating)
31 | 001F | 0 |  | 51 45 | Terminal 45 : Dehumidifier 0=disable 1=enable
32 | 20 | 0 |  | 51 46 | Terminal 46 : DHW Electric heater or Backup heater 0=DHW Electric heater 1=Backup heater
33 | 21 | 0
34 | 22 | 1